## Att-1
ATTACHMENT 01/ ĐÍNH KÈM 01: MTO/ DANH MỤC HÀNG HÓA (Đính kèm Kế hoạch mua sắm số: 18/KHCH-STG3)
No. | Material Number | Detail Specification | Unit | Q'ty | Remark
1 | B12C24BK | 24 twisted pair, 0.75mm² stranded (7/0.37), PE insulated, Plastic Tape, O/A Screen, PVC Sheath, SWA, Black PVC Sheath 300V. To EN 50288-7, Core Colours White, Black, and numbered pairs. | m | 2090
2 | B12C08BK | 8 twisted pair, 0.75mm² stranded (7/0.37), PE insulated, Plastic Tape, O/A Screen, PVC Sheath, SWA, Black PVC Sheath 300V. To EN 50288-7, Core Colours White, Black, and numbered pairs. | m | 1060
3 | B12D02BK | 2 twisted pair, 1.0mm² stranded (7/0.43), PE insulated, Plastic Tape, O/A Screen, PVC Sheath, SWA, Black PVC Sheath, 300V. To EN 50288-7, Core Colours White, Black, and numbered pairs. | m | 2255
4 | B12C04BK | 4 twisted pair, 0.75mm² stranded (7/0.37), PE insulated, Plastic Tape, O/A Screen, PVC Sheath, SWA, Black PVC Sheath 300V. To EN 50288-7, Core Colours White, Black and numbered pairs. | m | 2210
5 | B12C16BK | 16 twisted pair, 0.75mm² stranded (7/0.37), PE insulated, Plastic Tape, O/A Screen, PVC Sheath, SWA, Black PVC Sheath 300V. To EN 50288-7, Core Colours White, Black, and numbered pairs. | m | 515
6 | B32C16BK | 16 twisted pair, 0.75mm² stranded (7/0.37), Mica + XLPE insulated, Plastic Tape, O/A Screen, LSZH Sheath, SWA, Black LSZH Sheath 500V. Generally to EN 50288-7, Core Colours White, Black, and numbered pairs. Fire Resistant to IEC 60331-21. | m | 510
7 | B32C04BK | 4 twisted pair, 0.75mm² stranded (7/0.37), Mica + XLPE insulated, Plastic Tape, O/A Screen, LSZH Sheath, SWA, Black LSZH Sheath 500V. Generally to EN 50288-7, Core Colours White, Black, and numbered pairs. Fire Resistant to IEC 60331-21. | m | 1630
8 | C16C08BK | 8 twisted triad, 0.75mm² stranded (7/0.37), PE insulated, Individual triad Screen, Plastic Tape, O/A Screen, PVC Sheath, SWA, Black PVC Sheath 300V. To EN 50288-7, Core Colours White, Black, Red, and numbered triads. | m | 540
9 | C34C12BK | 12 twisted triad, 0.75mm² stranded (7/0.37), Mica + XLPE insulated, Individual triad Screen, Plastic Tape, O/A Screen, LSZH Sheath, SWA, Black LSZH Sheath 500V. Generally to EN 50288-7, Core Colours White, Black, Red, and numbered triads. Fire Resistant to IEC 60331-21. | m | 535
10 | C34C08BK | 8 twisted triad, 0.75mm² stranded (7/0.37), Mica + XLPE insulated, Individual triad Screen, Plastic Tape, O/A Screen, LSZH Sheath, SWA, Black LSZH Sheath 500V. Generally to EN 50288-7, Core Colours White, Black, Red, and numbered triads. Fire Resistant to IEC 60331-21. | m | 540
11 | B32G08BK | 8 twisted pair, 2.5mm² stranded (7/0.67), Mica + XLPE insulated, Plastic Tape, O/A Screen, LSZH Sheath, SWA, Black LSZH Sheath, 500V. Generally to EN 50288-7, Core Colours White, Black, and numbered pairs. Fire Resistant to IEC 60331-21. | m | 50
12 | C34C08BL | 8 twisted triad, 0.75mm² stranded (7/0.37), Mica + XLPE insulated, Individual triad Screen, Plastic Tape, O/A Screen, LSZH Sheath, SWA, Light Blue LSZH Sheath 500V. Generally to EN 50288-7, Core Colours White, Black, Red, and numbered triads. Fire Resistant to IEC 60331-21. | m | 1080
13 | C34C04BL | 4 twisted triad, 0.75mm² stranded (7/0.37), Mica + XLPE insulated, Individual triad Screen, Plastic Tape, O/A Screen, LSZH Sheath, SWA, Light Blue LSZH Sheath 500V. Generally to EN 50288-7, Core Colours White, Black, Red, and numbered triads. Fire Resistant to IEC 60331-21. | m | 1605
14 | A22J02BK | 2 core x 6.0mm² circular, stranded, XLPE insulated, PVC Bedding, SWA, Black PVC Sheath To IEC 60502-1. Core Colours, Red, Black. | m | 1100
15 | B12D01BK | Single twisted pair, 1.0mm² stranded (7/0.43), PE insulated, Plastic Tape, O/A Screen, PVC Sheath, SWA, Black PVC Sheath, 300V. To EN 50288-7, Core Colours White, Black. | m | 1920
16 | B32D01BK | Single twisted pair, 1.0mm² stranded (7/0.43), Mica + XLPE insulated, Plastic Tape, O/A Screen, LSZH Sheath, SWA, Black LSZH Sheath, 500V. Generally to EN 50288-7, Core Colours White, Black. Fire Resistant to IEC 60331-21. | m | 750
17 | B12G01BK | Single twisted pair, 2.5mm² stranded (7/0.67), PE insulated, Plastic Tape, Screen, PVC Sheath, SWA, Black PVC Sheath, 300V. Generally to EN 50288-7, Core Colours White, Black. | m | 300
18 | B32F02BK | 2 twisted pair, 1.5mm² stranded (7/0.53), Mica + XLPE insulated, Plastic Tape, O/A Screen, LSZH Sheath, SWA, Black LSZH Sheath, 500V. Generally to EN 50288-7, Core Colours White, Black, and numbered pairs. Fire Resistant to IEC 60331-21. | m | 200