## Cover
TỔNG CÔNG TY DẦU VIỆT NAM - CTCP
DỰ ÁN |  | MỞ RỘNG KHO XĂNG DẦU NGHI SƠN GIAI ĐOẠN 2
GÓI THẦU |  | THIẾT KẾ, CUNG CẤP VẬT TƯ, THIẾT BỊ VÀ THI CÔNG XÂY DỰNG CÔNG TRÌNH (EPC)
BẢNG THÔNG SỐ KỸ THUẬT CHO THIẾT BỊ ĐO LƯỜNG (DATASHEETS FOR INSTRUMENTS)
A1 | 21/12/2023 |  | Xuất bản để xem xét | N.X.Hung | N.D.Luong | P.Q.Phong
LXB. | Ngày |  | Mô tả | Thực hiện | Kiểm tra | Phê duyệt | PTH | PVOIL
Số tài liệu: PVOIL.NS-DD-IN-DAS-003
Tổng trang : 4 Trang (bao gồm trang bìa)

## Revision Log
THIẾT KẾ, CUNG CẤP VẬT TƯ, THIẾT BỊ VÀ THI CÔNG XÂY DỰNG CÔNG TRÌNH (EPC)
|  |  |  | Số tài liệu: PVOIL.NS-DD-IN-DAS-003 |  |  | Sheet: 02 of 06
KIỂM SOÁT THAY ĐỔI/BỔ SUNG
| LXB |  | Ngày |  | Mục | Nội dung thay đổi
| 1 |  | 21 / 12 / 2024 |  | Tất cả | Xuất bản để xem xét
21/12/2023

## PG
THIẾT KẾ, CUNG CẤP VẬT TƯ, THIẾT BỊ VÀ THI CÔNG XÂY DỰNG CÔNG TRÌNH (EPC)
[7 empty] | Số tài liệu: PVOIL.NS-DD-IN-DAS-003 | [10 empty] | Sheet: 01 of 02
DATASHEET FOR INSTRUMENT - PRESSURE GAUGE
Tag No. |  |  |  |  | : | See table below | [5 empty] | Client |  |  | : | Tổng công ty Dầu Việt Nam
Service |  |  |  |  | : | Oil Pump Station | [5 empty] | Plant Location |  |  | : | Khu kinh tế Nghi Sơn, tỉnh Thanh Hóa
P & ID No. |  |  |  |  | : | PVOIL.NS-FS-PR-PID-002 | [5 empty] | Facility |  |  | :
Specification No. |  |  |  |  | : | [6 empty] | No. of Units |  |  | :
SERVICE DESCRIPTION:
1 | GENERAL: | [9 empty] | 28 | BODY:
2 | Quantity: |  |  |  |  | See table below |  |  |  |  | 29 | Type: |  |  |  |  | Direct Reading
3 | Tag No.: |  |  |  |  | See table below |  |  |  |  | 30 |  | Others
4 | Location: |  |  |  |  | See table below |  |  |  |  | 31 | Mounting: |  |  |  |  | Stem
5 | Calibration Range: |  |  |  |  | See table below |  |  |  |  | 32 |  | Others
6 | Process Fluid: |  |  |  |  | See table below |  |  |  |  | 33 | Case Style: |  |  |  |  | Phenolic or AISI 316 TI
7 | PRESSURE ELEMENT: | [9 empty] | 34 |  | Others
8 | Accuracy: | [6 empty] | ± 0.1% F.S |  |  | 35 | Case Material: |  |  |  |  | Aluminum
9 |  |  | Others | [7 empty] | 36 |  | Others
10 | Overrange Protection.: | [6 empty] | 130% |  |  | 37 | Dial Size: |  |  |  |  | 150 mm
11 |  |  | Others | [7 empty] | 38 |  | Others
12 | Pressure Element: | [6 empty] | Bourdon |  |  | 39 | Dial Colour: |  |  |  |  | White
13 |  |  | Bellows |  |  |  |  | Diaphragm |  |  | 40 |  | Others
14 |  |  | Others | [7 empty] | 41 | Pointer: |  |  |  |  | Micrometer Adjustable
15 | Element Material: | [6 empty] | SS316 |  |  | 42 |  | Others
16 |  |  | Others | [7 empty] | 43 | Ring Type: |  |  |  |  | Bayonet
17 | Socket Material: | [6 empty] | SS316 |  |  | 44 |  | Others
18 |  |  | Others | [7 empty] | 45 | Blowout Protection: |  |  |  |  | Disc
19 | Movement Material: | [6 empty] | SS316 |  |  | 46 |  | Others
20 |  |  | Others | [7 empty] | 47 | Windown: |  |  |  |  | Shatterproof Glass
21 | Connection Location: | 21/12/2023 | [5 empty] | Lower |  |  | 48 |  | Others
22 |  |  | Others | [7 empty] | 49 | Liquid Filling: |  |  |  |  | Std Glycerine
23 | Process Connection: | [6 empty] | 1/2" NPT (M) |  |  | 50 |  | Others
24 |  |  | Others | [7 empty] | 51 | Valve Manifold: |  |  |  |  | Block & bleed valve 1/2" NPT
25 | Compensation Diaphragm: | [9 empty] | 52 |  | Others
26 | [10 empty] | 53 | Ingress Protection: |  |  |  |  | IP65
27 | [10 empty] | 54 |  | Others
55 | Item |  | Tag No |  |  | Range |  |  | Ope Pres. (Barg) | Temp. Rating |  |  | Fluid |  |  | Location |  | Remark
56 | [5 empty] | (Barg) |  |  | Nor. | (DegC)
57 | 1 |  |  | PG-9003 |  |  | -1 to 3 |  | ATM | 0 - 65 |  |  |  | DO |  | P-901 |  | PVOIL.NS-DD-PR-PID-002
58 | 2 |  |  | PG-9004 |  |  | 0 - 16 |  | 3 | 0 - 65 |  |  |  | DO |  | P-901 |  | PVOIL.NS-DD-PR-PID-002
59 | 3 |  |  | PG-5009 |  |  | 0-10 |  | 8 | 0 - 65 |  |  |  | FOAM |  | P-506 |  | PVOIL.NS-DD-SR-PID-001
60 | 4 |  |  | PG-5010 |  |  | 0-10 |  | 8 | 0 - 65 |  |  |  | FOAM |  | P-506 |  | PVOIL.NS-DD-SR-PID-001
61 | 5
62 | 6
63 | 7
64 | 8
65 | 9
66 | 10
67 | 11
68 | 12
69 | 13
70 | 14
71 | 15
72 | 16
73 | 17
74 | 18
75 | 19
76 | 20
77 | 21
78 | 22
83 | Notes:
84 | 1. VTA: Vendor to Advise
85 | 2. 316SS tags stamped with Tag No. in 15mm characters shall be permanently attached using 316SS screws or wire.
86 | 3. The device service for fire fighting system
87 | 4. Pressure gauge is absolute type
88 | 5. Reserve equipment

## LS
THIẾT KẾ, CUNG CẤP VẬT TƯ, THIẾT BỊ VÀ THI CÔNG XÂY DỰNG CÔNG TRÌNH (EPC)
|  |  |  | Số tài liệu: PVOIL.NS-DD-IN-DAS-003 | [10 empty] | Sheet: 02 of 02
DATASHEET FOR TRUCK LOADING SYSTEM - LEVEL SWITCH
Tag No. |  | : | See table below | [5 empty] | Client |  |  |  | : | Tổng công ty Dầu Việt Nam
Service |  | : | DO Storage tank | [5 empty] | Plant Location |  |  |  | : | Khu kinh tế Nghi Sơn, tỉnh Thanh Hóa
P & ID No. |  | : | PVOIL.NS-FS-PR-PID-001 | [5 empty] | Facility |  |  |  | :
Specification No. |  | : | [6 empty] | No. of Units |  |  |  | :
SERVICE DESCRIPTION:
1 | GENERAL | Tag Name | [8 empty] | LS-6002
2 |  | Type | [8 empty] | Vibration fork type
3 |  | Service | [8 empty] | DO Tank
4 |  | Line Number / Equipment No. | [8 empty] | TK-103
5 |  | Line size & Schedule | [8 empty] | -
6 |  | Area Classification | [8 empty] | Zone 1, IIA T3, IP65
7 | OPERATING CONDITIONS | Fluid | [8 empty] | DO
8 |  | Design Pressure. : |  |  |  |  | mmH2O
9 |  |  |  | Min |  | Max |  | -25 | [5 empty] | 75
10 |  | Temperature : |  |  |  |  | Deg C
11 |  |  |  | Min |  | Max. |  |  | 5 |  |  |  |  | 90
12 |  | S.G. / Mol. Weight:
13 |  | Viscosity |  |  |  |  | cP |  |  | 4.2
14 | SENSOR | Material: | [8 empty] | 316SS
15 |  | Insertion Length: |  |  |  |  | mm |  |  |  | 250
16 |  | Process Connection: | [8 empty] | 3", ASME 300#RF
17 | HOUSING | Material: | [8 empty] | Manufacturer Standard
18 |  | Explosion Protection: | [8 empty] | Atex II 1/2 G Eexia IIB, T6
19 |  | Protection Class | [8 empty] | IP 65 minimum
20 |  | Electrical Connection: | [8 empty] | 1/2" NPT (F)
21 | SWITCH | Quantity |  |  | Type |  |  |  | 2 |  |  |  |  | SPDT
22 |  | Contac Rating | [8 empty] | 5A, 48VDC
23 |  | Set Point |  |  | Hight |  |  |  | VTA |  |  | mm (Level decrease)
24 |  |  |  |  | Low |  |  |  | - |  |  | mm (Level decrease)
25 |  | Explosion Protection | [8 empty] | Atex II 1/2 G Eexia IIB, T6
26 |  | Electrical Connection | [8 empty] | 1/2" NPT (F)
27 |  | Power Supply : | [8 empty] | 24 VDC
28 |  | Protection Class | [8 empty] | IP 65 minimum
29 | PURCHASE | Manufacturer | [8 empty] | VTA
30 |  | Model | [8 empty] | VTA
31 |  | Certificate | [8 empty] | VTA
32 | Notes:
33 | 1. VTA -Vendor To Advise; N/A: Not Available
34 | 2. ATM-Atmosphere,AMB -Ambient
35 | 3. 316SS tags stamped with Tag No. in 15mm characters shall be permanently attached using 316SS screws or wire.
36
37
38
39
40
41
42
43
44
45
46
47
48