## COVER
TỔNG CÔNG TY DẦU VIỆT NAM
DỰ ÁN |  | MỞ RỘNG KHO XĂNG DẦU NGHI SƠN GIAI ĐOẠN 2
GÓI THẦU |  | THIẾT KẾ, CUNG CẤP VẬT TƯ, THIẾT BỊ VÀ THI CÔNG XÂY DỰNG CÔNG TRÌNH (EPC)
BẢNG DỮ LIỆU CHO VAN
A | 2024-04-10 |  | Xuất bản để xem xét
LXB | Ngày |  | Mô tả |  | Thực hiện | Kiểm tra | Phê duyệt |  | PTSC | PV OIL
|  |  |  | LIÊN DANH NHÀ THẦU |  |  |  | Số tài liệu:
|  |  |  | (PTSC THANH HOA/ TAM MINH) |  |  |  | PVOIL.NS-DD-PI-DAS-001
Tổng trang: 10 (bao gồm trang bìa)

## Index
DATASHEET FOR MANUAL VALVES
VALVE DATASHEET INDEX
| Valve Type |  | Valve Code | Size Range | Press. Rating | Piping Class | End Conn. | Body Material | Rev. | Sheet
| Ball Valve |  | VB8-001 | DN15-DN40 | 800# | 1A1, 1A2 | SW | CS | A | 3 of 10
| Gate Valve |  | VG8-001 | DN15-DN40 | 800# | 1A1 | SW | CS | A | 4 of 10
| Gate Valve |  | VG1-010 | DN50-DN250 | 150# | 1A1 | RF | CS | A | 5 of 10
| Check Valve |  | VC8-001 | DN15-DN40 | 800# | 1A1 | SW | CS | A | 6 of 10
| Check Valve |  | VC1-010 | DN50-DN250 | 150# | 1A1 | RF | CS | A | 7 of 10
| Butterfly Valve |  | VF1-010 | DN50-DN250 | 150# | 1A2 | RF | CS | A | 8 of 10
| Globe Valve |  | VL8-001 | DN15-DN40 | 800# | 1A1 | SW | CS | A | 9 of 10
| Wafer Valve |  | VW1-010 | DN50-DN250 | 150# | 1A2 | RF | CS | A | 10 of 10
For general material requirements, refer to Doc. No. Piping Material Class Specification

## VB8-001
DATASHEET FOR MANUAL VALVES
Valve Code |  |  | : | VB8-001 |  |  | Ball Valve |  |  |  | Client | :
Service |  |  | : | DO, FF | [6 empty] | Plant Location | :
P & ID No. |  |  | : | All | [6 empty] | Facility | :
Specification No. |  |  | : | [7 empty] | No. of Units | :
SERVICE DESCRIPTION:
1 | DESIGN REQUIREMENTS
2 | Valve Size |  |  |  | : | DN15 to DN40
3 | Valve Rating |  |  |  | : | API 602, BS EN ISO 15761: 2002, Class 800
4 | Bore |  |  |  | : | Reducer Port
5 | Design / Construction |  |  |  | : | Design to BS EN ISO 17292 and ASME B16.34
6 |  |  |  |  | : | Split body and Floating ball valve
7 |  |  |  |  | : | Anti-Static design and Fire safe design
8 |  |  |  |  | : | Blow-out proof stem
9 |  |  |  |  | : | Renewable seats
10 |  |  |  |  | :
11 | Pressure Design (bar) |  |  |  | : | 136.2 |  | 136.2 | 133.7 | 124.3
12 | Temperature Design (0C) |  |  |  | : | 0 |  | 38 | 50 | 100
13 | Piping Class |  |  |  | : | 1A1, 1A2
14 | End Connection |  |  |  | : | Socket Weld (SW) to ASME B16.11 with pipe pub (Note 5)
15 | Face to Face Standard |  |  |  | : | Manufacturer's standard
16 | Corrosion Allowance |  |  |  | : | 3mm
17 | Operator |  |  |  | : | Lever with position indicator
18
19 | MATERIAL REQUIREMENT
20 | Body / Adapter |  |  |  | : | ASTM A105
21 | Ball |  |  |  | : | ASTM A182 Gr. F316
22 | Stem |  |  |  | : | ASTM A182 F6a
23 | Body Seat ring |  |  |  | : | PTFE
24 | Anti-static Spring |  |  |  | : | Stainless Steel or X750
25 | Stem packing |  |  |  | : | PTFE / Graphite
26 | Stop plate / pin |  |  |  | : | ASTM A47 or Ductile Iron
27 | Lever |  |  |  | : | ASTM A47 or Ductile Iron
28 | Pipe pup |  |  |  | : | ASTM A53 Gr. B or A106 Gr.B SCH 80 with 100 mm length
29 | Bolting |  |  |  | : | ASTM A193 Gr. B7 / A194 Gr. 2H hot-dip galvanized or PTFE coated
30 | Gaskets |  |  |  | : | Spiral Wound SS316 + Graphite filler
31 | SUPPLEMENTARY REQUIREMENTS
32 | Painting |  |  |  | : | Yes, Accordance with Doc. No.: Painting Specification
33 | Fire safe design |  |  |  | : | Yes, As per API 6FA, API 6FB, API 607, BS 6755 Part II or ISO 10497
34 | Certification requirements |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
35 | Marking |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
36
37 | INSPECTION AND TESTING REQUIREMENTS
38 | Visual Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
39 | Magnetic Particle Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
40 | Liquid Penetrant Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
41 | Radiographic Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
42 | Pressure Test |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
43 | Toughness Tests |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
44
45 | NOTES
46 | 1. | Valve marking to be to MSS-SP-25. In addition to name plate, valve to be supplied with a stainless steel tag stamped
47 |  | securely fixed to the valve with non-corrosive wire
48 | 2. | Vendor to confirm and advise the all material components of valve to suit the gasoline, diesel, ethanol, fire water
49 |  | and fire foam services
50 | 3. | Any material testing requirement shall be complied with relative ASTM and ASME / ANSI
51 | 4. | For general material requirements, refer to Doc. No. Piping Material Class Specification
52 | 5. | The Pipe pups shall be welded on two side of socket weld valve. The pipe pups shall be supplied by valve vendor
53

## VG8-001
DATASHEET FOR MANUAL VALVES
Valve Code |  |  | : | VG8-001 |  | Gate Valve |  |  |  | Client | :
Service |  |  | : | DO | [5 empty] | Plant Location | :
P & ID No. |  |  | : | All | [5 empty] | Facility | :
Specification No. |  |  | : | [6 empty] | No. of Units | :
SERVICE DESCRIPTION:
1 | DESIGN REQUIREMENTS
2 | Valve Size |  |  |  | : | DN15 to DN40
3 | Valve Rating |  |  |  | : | API 602, BS EN ISO 15761: 2002, Class 800
4 | Bore |  |  |  | : | Full Port / Straight Pattern
5 | Design / Construction |  |  |  | : | Design to API 602 or BS EN ISO 15761 and ASME B16.34
6 |  |  |  |  | : | Outside Screw and Yoke (OS&Y), Rising Stem, Bolted Bonnet
7 |  |  |  |  | : | Back Seated Design, Stem Protector with open / shut indicator
8 |  |  |  |  | : | Solid Wedge
9 |  |  |  |  | : | Renewable Seat
10 |  |  |  |  | :
11 | Pressure Design (bar) |  |  |  | : | 136.2 | 136.2 | 133.7 | 124.3
12 | Temperature Design (0C) |  |  |  | : | 0 | 38 | 50 | 100
13 | Piping Class |  |  |  | : | 1A1
14 | End Connection |  |  |  | : | Socket Weld (SW) to ASME B16.11
15 | Face to Face Standard |  |  |  | : | Manufacturer's standard
16 | Corrosion Allowance |  |  |  | : | 3mm
17 | Operator |  |  |  | : | Handwheel
18
19 | MATERIAL REQUIREMENT
20 | Body / Bonnet |  |  |  | : | ASTM A105
21 | Disc / Wedge |  |  |  | : | ASTM A216 Gr. WCB Hard face with 13% Cr or Stellite #6 or SS316
22 | Stem |  |  |  | : | ASTM A182 F6a
23 | Body Seat ring |  |  |  | : | ASTM A105 Hard face with 13% Cr or Stellite #6
24 | Backseat ring |  |  |  | : | ASTM A276 Gr. 410
25 | Stem seal / packing |  |  |  | : | Graphite
26 | Yoke |  |  |  | : | ASTM A105
27 | Handwheel |  |  |  | : | ASTM A47 or Ductile Iron
28 | Bolting |  |  |  | : | ASTM A193 Gr. B7 / A194 Gr. 2H hot-dip galvanized or PTFE coated
29 | Gaskets |  |  |  | : | Spiral Wound SS316 + Graphite filler
30
31 | SUPPLEMENTARY REQUIREMENTS
32 | Painting |  |  |  | : | Yes, Accordance with Doc. No.: Painting Specification
33 | Fire safe design |  |  |  | : | Yes, As per API 6FA, API 6FB, API 607, BS 6755 Part II or ISO 10497
34 | Certification requirements |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
35 | Marking |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
36
37 | INSPECTION AND TESTING REQUIREMENTS
38 | Visual Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
39 | Magnetic Particle Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
40 | Liquid Penetrant Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
41 | Radiographic Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
42 | Pressure Test |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
43 | Toughness Tests |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
44
45 | NOTES
46 | 1. | Valve marking to be to MSS-SP-25. In addition to name plate, valve to be supplied with a stainless steel tag stamped
47 |  | securely fixed to the valve with non-corrosive wire
48 | 2. | Vendor to confirm and advise the all material components of valve to suit the gasoline, diesel, ethanol, fire water
49 |  | and fire foam services
50 | 3. | Any material testing requirement shall be complied with relative ASTM and ASME / ANSI
51 | 4. | For general material requirements, refer to Doc. No. Piping Material Class Specification
52
53

## VG1-010
DATASHEET FOR MANUAL VALVES
Valve Code |  |  | : | VG1-010 |  | Gate Valve |  |  |  | Client | :
Service |  |  | : | DO | [5 empty] | Plant Location | :
P & ID No. |  |  | : | All | [5 empty] | Facility | :
Specification No. |  |  | : | [6 empty] | No. of Units | :
SERVICE DESCRIPTION:
1 | DESIGN REQUIREMENTS
2 | Valve Size |  |  |  | : | DN50 to DN250
3 | Valve Rating |  |  |  | : | ASME Class 150
4 | Bore |  |  |  | : | Full Port / Straight Pattern
5 | Design / Construction |  |  |  | : | Design to API 600 and ASME B16.34
6 |  |  |  |  | : | Outside Screw and Yoke (OS&Y), Rising Stem, Bolted Bonnet
7 |  |  |  |  | : | Back Seated Design, Stem Protector with open / shut indicator
8 |  |  |  |  | : | Flexible Wedge
9 |  |  |  |  | : | Renewable Seat
10 |  |  |  |  | :
11 | Pressure Design (bar) |  |  |  | : | 19.6 | 19.6 | 19.2 | 17.7
12 | Temperature Design (0C) |  |  |  | : | 0 | 38 | 50 | 100
13 | Piping Class |  |  |  | : | 1A1
14 | End Connection |  |  |  | : | RF Flange to ASME B16.5
15 | Face to Face Standard |  |  |  | : | ASME B16.10
16 | Corrosion Allowance |  |  |  | : | 3mm
17 | Operator |  |  |  | : | Handwheel
18
19 | MATERIAL REQUIREMENT
20 | Body / Bonnet |  |  |  | : | ASTM A216 Gr. WCB
21 | Disc / Wedge |  |  |  | : | ASTM A216 Gr. WCB Hard face with 13% Cr or Stellite #6 or SS316
22 | Stem |  |  |  | : | ASTM A182 F6a
23 | Body Seat ring |  |  |  | : | ASTM A105 Hard face with 13% Cr or Stellite #6
24 | Backseat ring |  |  |  | : | ASTM A276 Gr. 410
25 | Stem seal / packing |  |  |  | : | Graphite
26 | Yoke |  |  |  | : | ASTM A216 Gr. WCB
27 | Handwheel |  |  |  | : | ASTM A47 or Ductile Iron
28 | Bolting |  |  |  | : | ASTM A193 Gr. B7 / A194 Gr. 2H hot-dip galvanized or PTFE coated
29 | Gaskets |  |  |  | : | Spiral Wound SS316 + Graphite filler
30
31 | SUPPLEMENTARY REQUIREMENTS
32 | Painting |  |  |  | : | Yes, Accordance with Doc. No.: Painting Specification
33 | Fire safe design |  |  |  | : | Yes, As per API 6FA, API 6FB, API 607, BS 6755 Part II or ISO 10497
34 | Certification requirements |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
35 | Marking |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
36
37 | INSPECTION AND TESTING REQUIREMENTS
38 | Visual Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
39 | Magnetic Particle Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
40 | Liquid Penetrant Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
41 | Radiographic Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
42 | Pressure Test |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
43 | Toughness Tests |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
44
45 | NOTES
46 | 1. | Valve marking to be to MSS-SP-25. In addition to name plate, valve to be supplied with a stainless steel tag stamped
47 |  | securely fixed to the valve with non-corrosive wire
48 | 2. | Raised Face (RF) Flange end connections shall have surface roughness between 3.2 µm and 6.3 µm
49 | 3. | Vendor to confirm and advise the all material components of valve to suit the gasoline, diesel, ethanol, fire water
50 |  | and fire foam services
51 | 4. | For general material requirements, refer to Doc. No. Piping Material Class Specification
52 | 5. | For general material requirements, refer to Doc. No. Piping Material Class Specification
53

## VC8-001
DATASHEET FOR MANUAL VALVES
Valve Code |  |  | : | VC8-001 |  | Piston check valve |  |  |  | Client | :
Service |  |  | : | DO, FF | [5 empty] | Plant Location | :
P & ID No. |  |  | : | All | [5 empty] | Facility | :
Specification No. |  |  | : | [6 empty] | No. of Units | :
SERVICE DESCRIPTION:
1 | DESIGN REQUIREMENTS
2 | Valve Size |  |  |  | : | DN15 to DN40
3 | Valve Rating |  |  |  | : | API 602, BS EN ISO 15761: 2002, Class 800
4 | Bore |  |  |  | : | Full Port / Straight Pattern
5 | Design / Construction |  |  |  | : | Design to BS EN ISO 15761 or API 602 and ASME B16.34
6 |  |  |  |  | : | Piston lift type and Spring return
7 |  |  |  |  | : | Bolted cover
8 |  |  |  |  | : | Renewable or integral Seat
9 |  |  |  |  | : | Flow Direction
10 |  |  |  |  | :
11 | Pressure Design (bar) |  |  |  | : | 136.2 | 136.2 | 133.7 | 124.3
12 | Temperature Design (0C) |  |  |  | : | 0 | 38 | 50 | 100
13 | Piping Class |  |  |  | : | 1A1, 1A2
14 | End Connection |  |  |  | : | Socket Weld (SW) to ASME B16.11
15 | Face to Face Standard |  |  |  | : | Manufacturer's standard
16 | Corrosion Allowance |  |  |  | : | 3mm
17 | Operator |  |  |  | : | N/A
18
19 | MATERIAL REQUIREMENT
20 | Body / Bonnet / Cover |  |  |  | : | ASTM A105
21 | Piston / Disc |  |  |  | : | ASTM A216 Gr. WCB Hard face with 13% Cr or Stellite #6
22 |  |  |  |  | : | or A276 Gr. 420 Hard face with 13% Cr or Stellite #6 or SS316
23 | Spring |  |  |  | : | Inconel 625 or X750
24 | Body Seat ring |  |  |  | : | ASTM A105 Hard face with 13% Cr or Stellite #6
25 | Bolting |  |  |  | : | ASTM A193 Gr. B7 / A194 Gr. 2H hot-dip galvanized or PTFE coated
26 | Gaskets |  |  |  | : | Spiral Wound SS316 + Graphite filler
27
28
29
30
31 | SUPPLEMENTARY REQUIREMENTS
32 | Painting |  |  |  | : | Yes, Accordance with Doc. No.: Painting Specification
33 | Fire safe design |  |  |  | : | Yes, As per API 6FA, API 6FB, API 607, BS 6755 Part II or ISO 10497
34 | Certification requirements |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
35 | Marking |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
36
37 | INSPECTION AND TESTING REQUIREMENTS
38 | Visual Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
39 | Magnetic Particle Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
40 | Liquid Penetrant Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
41 | Radiographic Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
42 | Pressure Test |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
43 | Toughness Tests |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
44
45 | NOTES
46 | 1. | Valve marking to be to MSS-SP-25. In addition to name plate, valve to be supplied with a stainless steel tag stamped
47 |  | securely fixed to the valve with non-corrosive wire
48 | 2. | Vendor to confirm and advise the all material components of valve to suit the gasoline, diesel, ethanol, fire water
49 |  | and fire foam services
50 | 3. | Any material testing requirement shall be complied with relative ASTM and ASME / ANSI
51 | 4. | For general material requirements, refer to Doc. No. Piping Material Class Specification
52
53

## VC1-010
DATASHEET FOR MANUAL VALVES
Valve Code |  |  | : | VC1-010 |  | Swing check valve |  |  |  | Client | :
Service |  |  | : | DO | [5 empty] | Plant Location | :
P & ID No. |  |  | : | All | [5 empty] | Facility | :
Specification No. |  |  | : | [6 empty] | No. of Units | :
SERVICE DESCRIPTION:
1 | DESIGN REQUIREMENTS
2 | Valve Size |  |  |  | : | DN50 to DN250
3 | Valve Rating |  |  |  | : | ASME Class 150
4 | Bore |  |  |  | : | Full Port / Straight Pattern
5 | Design / Construction |  |  |  | : | Design to BS 1868 or API 6D and ASME B16.34
6 |  |  |  |  | : | Swing type disc
7 |  |  |  |  | : | Bolted cover
8 |  |  |  |  | : | Renewable Seat
9 |  |  |  |  | : | Flow Direction
10 |  |  |  |  | :
11 | Pressure Design (bar) |  |  |  | : | 19.6 | 19.6 | 19.2 | 17.7
12 | Temperature Design (0C) |  |  |  | : | 0 | 38 | 50 | 100
13 | Piping Class |  |  |  | : | 1A1
14 | End Connection |  |  |  | : | RF Flange to ASME B16.5
15 | Face to Face Standard |  |  |  | : | ASME B16.10
16 | Corrosion Allowance |  |  |  | : | 3mm
17 | Operator |  |  |  | : | N/A
18
19 | MATERIAL REQUIREMENT
20 | Body / Bonnet |  |  |  | : | ASTM A216 Gr. WCB
21 | Disc / Clapper disc |  |  |  | : | ASTM A216 Gr. WCB Hard face with 13% Cr or Stellite #6 or SS316
22 | Clapper disc arm / Hinge |  |  |  | : | ASTM A216 Gr. WCB
23 | Body Seat ring |  |  |  | : | ASTM A105 Hard face with 13% Cr or Stellite #6
24 | Shaft / Hinge pin |  |  |  | : | ASTM A276 Gr. 410 or A216 Gr. WCB Hard face with 13% Cr or Stellite #6
25 | Disc nut & washer |  |  |  | : | ASTM A276 Gr. 410 or A216 Gr. WCB Hard face with 13% Cr or Stellite #6
26 | Bolting |  |  |  | : | ASTM A193 Gr. B7 / A194 Gr. 2H hot-dip galvanized or PTFE coated
27 | Gaskets |  |  |  | : | Spiral Wound SS316 + Graphite filler
28
29
30
31 | SUPPLEMENTARY REQUIREMENTS
32 | Painting |  |  |  | : | Yes, Accordance with Doc. No.: Painting Specification
33 | Fire safe design |  |  |  | : | Yes, As per API 6FA, API 6FB, API 607, BS 6755 Part II or ISO 10497
34 | Certification requirements |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
35 | Marking |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
36
37 | INSPECTION AND TESTING REQUIREMENTS
38 | Visual Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
39 | Magnetic Particle Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
40 | Liquid Penetrant Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
41 | Radiographic Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
42 | Pressure Test |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
43 | Toughness Tests |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
44
45 | NOTES
46 | 1. | Valve marking to be to MSS-SP-25. In addition to name plate, valve to be supplied with a stainless steel tag stamped
47 |  | securely fixed to the valve with non-corrosive wire
48 | 2. | Raised Face (RF) Flange end connections shall have surface roughness between 3.2 µm and 6.3 µm
49 | 3. | Vendor to confirm and advise the all material components of valve to suit the gasoline, diesel, ethanol, fire water
50 |  | and fire foam services
51 | 4. | For general material requirements, refer to Doc. No. Piping Material Class Specification
52 | 5. | For general material requirements, refer to Doc. No. Piping Material Class Specification
53

## VF1-010
DATASHEET FOR MANUAL VALVES
Valve Code |  |  | : | VF1-010 |  | Butterfly Valve |  |  |  | Client | :
Service |  |  | : | FF | [5 empty] | Plant Location | :
P & ID No. |  |  | : | All | [5 empty] | Facility | :
Specification No. |  |  | : | [6 empty] | No. of Units | :
SERVICE DESCRIPTION:
1 | DESIGN REQUIREMENTS
2 | Valve Size |  |  |  | : | DN50 to DN200
3 | Valve Rating |  |  |  | : | ASME Class 150
4 | Bore |  |  |  | : | Standard bore
5 | Design / Construction |  |  |  | : | Design to API 609 (Category A or B) and ASME B16.34
6 |  |  |  |  | : | Eccentric or concentric disc configuration
7 |  |  |  |  | : | Wafer or lug type with through drilled hole to ASME B16.5
8 |  |  |  |  | : | Multi-position "locking lever" of the notched plate design
9 |  |  |  |  | : | Double offset or triple offset design is preferred
10 |  |  |  |  | : | Fire safe design
11 |  |  |  |  | : | Blow-out proof stem
12 | Pressure Design (bar) |  |  |  | : | 19.6 | 19.6 | 19.2 | 17.7
13 | Temperature Design (0C) |  |  |  | : | 0 | 38 | 50 | 100
14 | Piping Class |  |  |  | : | 1A2
15 | End Connection |  |  |  | : | RF Flange to ASME B16.5
16 | Face to Face Standard |  |  |  | : | ASME B16.10
17 | Corrosion Allowance |  |  |  | : | 3mm
18 | Operator |  |  |  | : | Lever with position indicator
19 |  |  |  |  | : | Handwheel + Gear with position indicator
20 |  |  |  |  | :
21 | MATERIAL REQUIREMENT
22 | Body / Bonnet |  |  |  | : | ASTM A216 Gr. WCB
23 | Disc / Wedge |  |  |  | : | ASTM A216 Gr. WCB Hard face with 13% Cr or Stellite #6 or SS316
24 | Stem |  |  |  | : | ASTM A182 F6a
25 | Body Seat ring |  |  |  | : | PTFE
26 | Stem seal / packing |  |  |  | : | PTFE / Graphite
27 | Lever / Handwheel |  |  |  | : | ASTM A47 or Ductile Iron
28 | Bolting |  |  |  | : | ASTM A193 Gr. B7 / A194 Gr. 2H hot-dip galvanized or PTFE coated
29 | Gaskets |  |  |  | : | Spiral Wound SS316 + Graphite filler
30 |  |  |  |  | :
31
32 | SUPPLEMENTARY REQUIREMENTS
33 | Painting |  |  |  | : | Yes, Accordance with Doc. No.: Painting Specification
34 | Fire safe design |  |  |  | : | Yes, As per API 6FA, API 6FB, API 607, BS 6755 Part II or ISO 10497
35 | Certification requirements |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
36 | Marking |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
37
38 | INSPECTION AND TESTING REQUIREMENTS
39 | Visual Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
40 | Magnetic Particle Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
41 | Liquid Penetrant Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
42 | Radiographic Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
43 | Pressure Test |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
44 | Toughness Tests |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
45
46 | NOTES
47 | 1. | Valve marking to be to MSS-SP-25. In addition to name plate, valve to be supplied with a stainless steel tag stamped
48 |  | securely fixed to the valve with non-corrosive wire
49 | 2. | Raised Face (RF) Flange end connections shall have surface roughness between 3.2 µm and 6.3 µm
50 | 3. | Vendor to confirm and advise the all material components of valve to suit the fire water and fire foam services
51 | 4. | For general material requirements, refer to Doc. No. Piping Material Class Specification
52 | 5. | For general material requirements, refer to Doc. No. Piping Material Class Specification
53

## VL8-001
DATASHEET FOR MANUAL VALVES
Valve Code |  |  | : | VL8-001 |  |  | Globe Valve |  |  |  | Client | :
Service |  |  | : | DO | [6 empty] | Plant Location | :
P & ID No. |  |  | : | All | [6 empty] | Facility | :
Specification No. |  |  | : | [7 empty] | No. of Units | :
SERVICE DESCRIPTION:
1 | DESIGN REQUIREMENTS
2 | Valve Size |  |  |  | : | DN15 to DN40
3 | Valve Rating |  |  |  | : | API 602, BS EN ISO 15761: 2002, Class 800
4 | Bore |  |  |  | : | STANDARD
5 | Design / Construction |  |  |  | : | BS EN ISO 15761:2002 / BS 1873 ( RATING AS PER ASME B 16.34 AS A MINIMUM )
6 |  |  |  |  | : | OUTSIDE SCREW & YOKE (OS&Y)
7 |  |  |  |  | : | RISING STEM
8 |  |  |  |  | : | BALL TYPE DISC
9 |  |  |  |  | : | BOLTED BONNET
10 | [5 empty] | HARDFACED, RENEWABLE SEATS
11 |  |  |  |  | : | FIRE SAFE ( DESIGN )
12 | Pressure Design (bar) |  |  |  | : | 136.2 |  | 136.2 | 133.7 | 124.3
13 | Temperature Design (0C) |  |  |  | : | 0 |  | 38 | 50 | 100
14 | Piping Class |  |  |  | : | 1A1
15 | End Connection |  |  |  | : | Socket Weld (SW) to ASME B16.11 with pipe pub (Note 5)
16 | Face to Face Standard |  |  |  | : | ASME B16.10
17 | Corrosion Allowance |  |  |  | : | 3mm
18 | Operator |  |  |  | : | HANDWHEEL (LOCK OPEN/LOCK CLOSE FACILITY)
19
20 | MATERIAL REQUIREMENT
21 | BODY / BONNET |  |  |  | : | ASTM A105
22 | DISC |  |  |  |  | 13% Cr - ASTM A182 Gr.F6A HARDFACED WITH TUNGSTEN CARBIDE
23 | STEM |  |  |  |  | 13% Cr - ASTM A182 Gr.F6A OR ASTM A276 Gr.410 , WITH 0.003 " E.N.P
24 | SEATS |  |  |  |  | 13% Cr - ASTM A182 Gr.F6A HARDFACED WITH STELLITE 6 OR SOLID STELLITE
25 | STEM SEALS/PACKING |  |  |  |  | REINFORCED GRAPHOIL
26 | FLOW DIRECTION |  |  |  |  | YES
27 | EXTENDED STEM |  |  |  |  | IF REQUIRED
28
29 | Pipe pup |  |  |  | : | ASTM A53 Gr. B or A106 Gr.B SCH 80 with 100 mm length
30 | Bolting |  |  |  | : | ASTM A193 Gr. B7 / A194 Gr. 2H hot-dip galvanized or PTFE coated
31 | Gaskets |  |  |  | : | Spiral Wound SS316 + Graphite filler
32 | SUPPLEMENTARY REQUIREMENTS
33 | Painting |  |  |  | : | Yes, Accordance with Doc. No.: Painting Specification
34 | Fire safe design |  |  |  | : | Yes, As per API 6FA, API 6FB, API 607, BS 6755 Part II or ISO 10497
35 | Certification requirements |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
36 | Marking |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
37
38 | INSPECTION AND TESTING REQUIREMENTS
39 | Visual Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
40 | Magnetic Particle Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
41 | Liquid Penetrant Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
42 | Radiographic Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
43 | Pressure Test |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
44 | Toughness Tests |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
45
46 | NOTES
47 | 1. | Valve marking to be to MSS-SP-25. In addition to name plate, valve to be supplied with a stainless steel tag stamped
48 |  | securely fixed to the valve with non-corrosive wire
49 | 2. | Vendor to confirm and advise the all material components of valve to suit the gasoline, diesel, ethanol, fire water
50 |  | and fire foam services
51 | 3. | For general material requirements, refer to Doc. No. Piping Material Class Specification
52 | 4. | For general material requirements, refer to Doc. No. Piping Material Class Specification
53 | 5. | The Pipe pups shall be welded on two side of socket weld valve. The pipe pups shall be supplied by valve vendor
54

## VW1-010
DATASHEET FOR MANUAL VALVES
Valve Code |  |  | : | VW1-010 |  | WAFER Valve |  |  |  | Client | :
Service |  |  | : | FF | [5 empty] | Plant Location | :
P & ID No. |  |  | : | All | [5 empty] | Facility | :
Specification No. |  |  | : | [6 empty] | No. of Units | :
SERVICE DESCRIPTION:
1 | DESIGN REQUIREMENTS
2 | Valve Size |  |  |  | : | DN50 to DN200
3 | Valve Rating |  |  |  | : | ASME Class 150
4 | Bore |  |  |  | : | Standard bore
5 | Design / Construction |  |  |  | : | API 6D ( RATING AS PER ASME B 16.34 AS A MINIMUM )
6 |  |  |  |  | : | WAFER TYPE, LUGGED DRILLED-THROUGH
7 |  |  |  |  | : | DUAL PLATE
8 |  |  |  |  | : | SPRING RETURN
9 |  |  |  |  | : | RENEWABLE SEAT
10 |  |  |  |  | : | RETAINERLESS DESIGN
11 |  |  |  |  | :
12 | Pressure Design (bar) |  |  |  | : | 19.6 | 19.6 | 19.2 | 17.7
13 | Temperature Design (0C) |  |  |  | : | 0 | 38 | 50 | 100
14 | Piping Class |  |  |  | : | 1A2
15 | End Connection |  |  |  | : | RF Flange to ASME B16.5
16 | Face to Face Standard |  |  |  | : | ASME B16.10
17 | Corrosion Allowance |  |  |  | : | 3mm
#REF! |  |  |  |  | :
#REF! | MATERIAL REQUIREMENT
#REF! | MATERIALS |  |  |  | : | FORGED |  | CARBON STEEL ASTM A105N
#REF! | BODY |  |  |  | : | CAST |  | CARBON STEEL ASTM A216 Gr.WCB / WCC
[5 empty] | : | ASTM A 182 GR. F6A HARDFACED WITH STELLITE 6 OR SOLID STELLITE
| PLATES |  |  |  | : | INCONEL 625 OR X750
| SPRING |  |  |  | : | ASTM A 564 GR. 630 WITH 0.003 " E.N.P
| PINS |  |  |  | : | ASTM A 105N/ASTM A216 Gr. WCB/WCC HARDFACED WITH TUNGSTEN CARBIDE
#REF! | SEATS |  |  |  | :
#REF! |  |  |  |  | : | BOLTS |  | ASTM A193 Gr. B7, HOT DIP SPUN GALVANISED +PTFE
#REF! | BOLTING |  |  |  | : | NUTS |  | ASTM A194 Gr. 2H HEAVY HEX, HOT DIP SPUN GALVANISED +PTFE
#REF! |  |  |  |  | :
#REF! | FLOW DIRECTION |  |  |  | : | YES
#REF! |  |  |  |  | :
#REF! |  |  |  |  | :
#REF!
#REF! | SUPPLEMENTARY REQUIREMENTS
#REF! | Painting |  |  |  | : | Yes, Accordance with Doc. No.: Painting Specification
#REF! | Fire safe design |  |  |  | : | Yes, As per API 6FA, API 6FB, API 607, BS 6755 Part II or ISO 10497
#REF! | Certification requirements |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
#REF! | Marking |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
#REF!
#REF! | INSPECTION AND TESTING REQUIREMENTS
#REF! | Visual Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
#REF! | Magnetic Particle Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
#REF! | Liquid Penetrant Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
#REF! | Radiographic Examination |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
#REF! | Pressure Test |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
#REF! | Toughness Tests |  |  |  | : | Yes, As per Doc. No.: Specification for Manual Valve
#REF!
#REF! | NOTES
#REF! | 1. | Valve marking to be to MSS-SP-25. In addition to name plate, valve to be supplied with a stainless steel tag stamped
#REF! |  | securely fixed to the valve with non-corrosive wire
#REF! | 2. | Raised Face (RF) Flange end connections shall have surface roughness between 3.2 µm and 6.3 µm
#REF! | 3. | Vendor to confirm and advise the all material components of valve to suit the fire water and fire foam services
#REF! | 4. | For general material requirements, refer to Doc. No. Piping Material Class Specification
#REF! | 5. | For general material requirements, refer to Doc. No. Piping Material Class Specification
#REF!