## Cover
TỔNG CÔNG TY DẦU VIỆT NAM
DỰ ÁN |  | MỞ RỘNG KHO XĂNG DẦU NGHI SƠN GIAI ĐOẠN 2
GÓI THẦU |  | THIẾT KẾ, CUNG CẤP VẬT TƯ, THIẾT BỊ VÀ THI CÔNG XÂY DỰNG CÔNG TRÌNH (EPC)
BẢNG DỮ LIỆU CHO BƠM CỨU HỎA (FIRE FIGHTING PUMP DATSHEET)
| 29/05/2025 |  | Xuất bản để mua sắm | LNT | PAD | PQP
A | 2024-10-12 |  | Xuất bản để xem xét | LNT | PAD | PQP
LXB. | Ngày |  | Mô tả | Thực hiện | Kiểm tra | Phê duyệt | CECO | PVOIL
|  |  | LIÊN DANH NHÀ THẦU (PTSC THANH HOA/ TAM MINH) |  |  | Số tài liệu: PVOIL.NS-DD-PR-DAS-001
Tổng trang : 03 (bao gồm trang bìa)

## Revision Log
THIẾT KẾ CƠ SỞ DỰ ÁN: MỞ RỘNG KHO XĂNG DẦU NGHI SƠN GIAI ĐOẠN 2
Số tài liệu: PVOIL.NS-DD-PR-DAS-001
KIỂM SOÁT THAY ĐỔI/ BỔ SUNG
LXB |  | Ngày | Mục | Nội dung thay đổi
A |  | 2024-10-12 |  | Xuất bản để xem xét
A |  | 29/05/2025 |  | Xuất bản để mua sắm
Số tài liệu: PVOIL.NS-DD-PR-DAS-001

## CENTRIFUGAL PUMP
THIẾT KẾ CƠ SỞ DỰ ÁN: MỞ RỘNG KHO XĂNG DẦU NGHI SƠN GIAI ĐOẠN 2
Số tài liệu: PVOIL.NS-DD-PR-DAS-001
PROCESS DATASHEETS FOR PUMPS
Tag No. |  |  |  | : | P-506 |  |  |  | Client | : | PVOIL
Service |  |  |  | : | Fire Water Pump |  |  |  | Plant Location | : | THANH HOA
P & ID No. |  |  |  | : | PVOIL.NS-FS-SR-DWG-001 |  |  |  | Facility | : | -
Specification No. |  |  |  | : | PVOIL.NS-DD-ME-SPC-001 |  |  |  | No. of Units | : | 1x100%
SERVICE DESCRIPTION:
| I | TAG NUMBER | [6 empty] | P-506
|  | SERVICE | [6 empty] | Foam
|  | TYPE : | [6 empty] | CENTRIFUGAL
|  | NUMBER REQUIRED |  |  |  | OPER./STANDBY |  |  | 1/0
1 | II | PROPERTIES OF LIQUID
2 | 1 | PUMPING TEMPARATURE: | [5 empty] | ° C | AMB
3 | 2 | VISCOSITY AT PUMPING TEMP: | [5 empty] | cP | 1
4 | 3 | VAPOUR PRESSURE AT PUMPING TEMP. : | [5 empty] | kPa | 7.3
5 | 4 | LIQUID DENSITY AT PUMPING TEMP. : | [5 empty] | kg/m3 | 1080
6 | 5 | PRESENCE OF TOXIC COMPONENT : | [5 empty] | YES/NO | NO
7 | 6 | PRESENCE OF H2S COMPONENTS : | [5 empty] | YES/NO | NO
8 | 7 | SOLIDS IN SUSPENSION : | [5 empty] | YES/NO | NO
9 | 8 | CORROSIVE / EROSIVE | [5 empty] | YES/NO | NO
10 | III | SIZE ENVIRONMENT DATA
11 | 1 | ALTITUDE | [5 empty] | m | 1
12 | 2 | BAROMETER | [5 empty] | kPa | 101.3
13 | 3 | RANGE OF AMBIENT TEMPS: MIN./MAX. | [5 empty] | ° C | 12/ 41.4
14 | 4 | RELATIVE HUMIDITY: MIN./MAX. | [5 empty] | % | 34/90
15 | IV | OPERATING CONDITIONS :
16 | 1 | FLOWRATE : | NORMAL |  |  |  |  | m3/hr | 60
17 | 2 | MAX. | [5 empty] | m3/hr | 90 - VTA
18 | 3 | SUCTION PRESSURE : | Min/Max |  |  |  |  | kPaa | 101
19 | 4 | DISCHARGE PRESSURE : | [5 empty] | kPaa | 901
20 | 5 | DIFFERENTIAL PRESSURE : | [5 empty] | kPa | 800
21 | 6 | DIFFERENTIAL HEAD REQUIRED: | [5 empty] | mlc | 75.5087
22 | 7 | NPSH AVAILABLE : | [5 empty] | mlc | 8.87
23 | 8 | NPSH REQUIRED | [5 empty] | mlc | VTA
24 | 9 | ESTIMATED EFFICIENCY | [5 empty] | % | 70
25 | 10 | ESTIMATED SHAFT POWER | [5 empty] | KW | VTA
26 | 11 | ESTIMATED MOTOR POWER | [5 empty] | KW | VTA
27 | 12 | DESIGN CODE | [6 empty] | VTA
28 | 13 | DESIGN PRESSURE | [5 empty] | mH20 | 80
29 | 14 | DESIGN TEMPARATURE | [5 empty] | ° C | 65
30 | V | MECHANICAL DATA
31 | 1 | MATERIAL OF CONST. |  |  |  |  | CASING |  | -
32 | 2 | [5 empty] | IMPELLER |  | -
33 | VI | DRIVER
34 |  | TYPE : | [6 empty] | ELEC. MOTOR
NOTES
35 | 1) | VTA = VENDOR to advise, VTC= VENDOR to confirm, N/A= Not Applicable
36 | 2) | All auxiliaries shall be powered by the engine itself.
37 | 3) Max flowrate (90 m3/h) is 150% design flowrate (60 m3/h) at min 65 % design pressure (52 mH2O)
38 | 4) | Diesel engine shall fully comply to to NFPA 20, QCVN 02:2020/BCA, UL listed/FM approved, and
39 |  | additional engine safety devices, if any.
40 | 5) | Expansion tank for Radiator: liberally sized, provided with fill, over flow, drain and level indication &alarm.
41 | 6) | The capacity of the fuel tank shall be such that the engine can operate on full power based on
42 |  | NFPA 20, QCVN 02:2020/BCA requirements.
43 | 7) | Vendor shall also advise additional engine safety devices, if any. Unit control panel shall be IP65,
44 |  | suitable for outdoor shelter.