## GAUGE HATCH
DESIGN, PROCURREMENT AND CONSTRUCTION FOR NGHI SON PETROLEUM STORAGE PROJECT
|  |  |  | Datasheet.No: PVOIL.NS-DD-IN-DAS-001 |  |  |  |  | Rev: A | Sheet: 3 of 5
DATASHEET FOR INSTRUMENT - GAUGE HATCH
Tag No. |  | : | See table below |  |  | Client | : | PV OIL
Service |  | : | Tank Gauging |  |  | Plant Location | : | Thanh hoa Province
P & ID No. |  | : | PVOIL.NS-FS-PR-PID-001 |  |  | Facility | : | Nghi son Petroleum Storage
Specification No. |  | : |  |  |  | No. of Units | : | N/A
SERVICE DESCRIPTION:
1 | GENERAL | Tag Name |  |  | -
2 |  | Line Number / Equipment No. |  |  | TK-103
3 |  | Quantity |  |  | 1
4 |  | Service |  |  | DO Tank TK-103
5 |  | Fluid & Fluid State |  |  | E100
6 |  | P&ID No |  |  | PVOIL.NS-FS-PR-PID-001
7 |  | Design Temperature (˚C) |  |  | 5 to 70
8 |  | Design Pressure (mmH2O) |  |  | -25 / 75
9 |  | Operating Pressure |  |  | ATM
10 | GAUGE HATCH COVER SPECIFICATION | Body and cover material |  |  | ASTM A216 WBC
11 |  | Seat material |  |  | Teflon or Equivalent
12 |  | Eye bolt & buttfly nut |  |  | SS 304
13 |  | HINGE PINE |  |  | SS 304
14 |  | Size |  |  | 6"
15 |  | Connection |  |  | RF Flange, #150
16 |  | Model |  |  | VTA
17 |  | Type |  |  | Lock Down & Non Sparking
18 |  | Painting |  |  | Refer "PVOIL.NS-DD-PI-SPC-003"
19
20 | Notes:
21 | 1.VTA: Vendor to Advise
22 | 2. 316SS tag stamped with Tag No., service, PO No. and manufacturers name plate in 15mm characters shall be permanently
23 | 3. Vendor to refer Process datasheet for tank and piping level settings and dimension
24
25
26
27

## BREATHER VALVE
DESIGN, PROCURREMENT AND CONSTRUCTION FOR NGHI SON PETROLEUM STORAGE PROJECT
|  |  |  | Datasheet.No: PVOIL.NS-DD-IN-DAS-001 | [10 empty] | Rev: A |  | Sheet: 4 of 5
DATASHEET FOR INSTRUMENT - BREATHER VALVE
Tag No. |  | : | See table below | [8 empty] | Client | : | PV OIL
Service |  | : | Tank Gauging | [8 empty] | Plant Location | : | Thanh hoa Province
P & ID No. |  | : | PVOIL.NS-FS-PR-PID-001 | [8 empty] | Facility | : | Nghi son Petroleum Storage
Specification No. |  | : | [9 empty] | No. of Units | : | N/A
SERVICE DESCRIPTION:
1 | GENERAL | Tag Name | [8 empty] | BTV - 6001 |  |  |  |  | BTV - 6002
2 |  | Line Number / Equipment No. | [8 empty] | TK-103 |  |  |  |  | TK-103
3 |  | Line size & Schedule | [8 empty] | - |  |  |  |  | -
4 |  | Equip./Vessel Protected | [8 empty] | DO Tank TK-103 |  |  |  |  | DO Tank TK-103
5 |  | Valve Type | [8 empty] | Breather Valve |  |  |  |  | Breather Valve
6 |  | P&ID No | [8 empty] | PVOIL.NS-FS-PR-PID-001 |  |  |  |  | PVOIL.NS-FS-PR-PID-001
7 | SERVICE CONDITION | Fluid & Fluid State | [8 empty] | E100 |  |  |  |  | E100
8 |  | Sizing Basis | [8 empty] | In/ Out Breathing |  |  |  |  | In/ Out Breathing
9 |  | Corrosive Constituents | [8 empty] | Yes |  |  |  |  | Yes
10 |  | Required Capacity | [6 empty] | Kg/h |  | - |  |  |  |  | -
11 |  | SG. | .@ | Rel. | Temp |  |  | Mol.WT. |  |  | 0.732 |  |  |  |  | 0.732
12 |  | Pressure (Min/Max) | [5 empty] | mm H2O |  |  | -25 to 75 |  |  |  |  | -25 to 75
13 |  | Temp.(Min/Max) | [7 empty] | °C | AMB |  |  |  |  | ATM
14 |  | Valve Discharges To | [8 empty] | ATM
15 |  | Back Pressure: |  |  |  | Const./Variable |  |  |  |  | - |  |  |  |  | -
16 |  | Set Pressure | [5 empty] | kg/cm2g |  |  | - |  |  |  |  | -
17 |  | Cold Bench Test Pressure | [8 empty] | VTA |  |  |  |  | VTA
18 |  | % Over Pressure |  |  |  |  | %Blown Down |  |  |  | - |  |  |  |  | -
19 |  | Compressibility Factor | [8 empty] | - |  |  |  |  | -
20 |  | Cp/Cv | [8 empty] | - |  |  |  |  | -
21 |  | Viscosity @ Rel Temp | [6 empty] | Cp |  | 0.91 |  |  |  |  | 0.91
22 |  | Vessel Wall Temp |  |  |  |  | Surf. Area cm2 |  |  |  | - |  |  |  |  | -
23 | VALVE | Type | [8 empty] | Conventional |  |  |  |  | Conventional
24 |  | Nozzle | [8 empty] | Full nozzle |  |  |  |  | Full nozzle
25 |  | Bonnet Type | [8 empty] | Closed |  |  |  |  | Closed
26 |  | Process Connection : Size & Rating | [8 empty] | 6" & 150# |  |  |  |  | 6" & 150#
27 |  | Facing & Finish | [8 empty] | Flanged, RF Serrated |  |  |  |  | Flanged, RF Serrated
28 |  | Cap Over Adjusting Bolt | [8 empty] | Reqd |  |  |  |  | Reqd
29 |  | Lever | [8 empty] | VTA |  |  |  |  | VTA
30 |  | Test Gag | [8 empty] | If Reqd |  |  |  |  | If Reqd
31 | MATERIAL | Body & Bonnet Material | [8 empty] | ASTM A216 WBC |  |  |  |  | ASTM A216 WBC
32 |  | Nozzle & Disc | [8 empty] | SS 316 |  |  |  |  | SS 316
33 |  | Bellows | [8 empty] | N/A |  |  |  |  | N/A
34 |  | Spring | [8 empty] | SS 316 |  |  |  |  | SS 316
35 |  | Resilient Seat Seal | [8 empty] | SS 316 Stellited |  |  |  |  | SS 316 Stellited
36 | BASIS | Code | [8 empty] | N/A |  |  |  |  | N/A
37 |  | Basis Of selection | [8 empty] | Operating |  |  |  |  | Operating
38 | ORIFICE | Calculated Area | [7 empty] | cm2 | VTA |  |  |  |  | VTA
39 |  | Selected Area | [7 empty] | cm2 | VTA |  |  |  |  | VTA
40 |  | Orifice Designation | [8 empty] | VTA |  |  |  |  | VTA
41 |  | No. Of Valve Selected For Cap. | [8 empty] | 1 |  |  |  |  | 1
42 |  | Total Area | [7 empty] | cm2 | VTA |  |  |  |  | VTA
43 |  | Actual Capacity | [7 empty] | kg/h | VTA |  |  |  |  | VTA
44 | PURCHASE | Manufacturer | [8 empty] | VTA |  |  |  |  | VTA
45 |  | Model | [8 empty] | VTA |  |  |  |  | VTA
46 |  | Certificate | [8 empty] | VTA |  |  |  |  | VTA
47
48 | Notes:
49 | 1.VTA: Vendor to Advise
50 | 2. 316SS tag stamped with Tag No., service, PO No. and manufacturers name plate in 15mm characters shall be permanently
51 | 3. Vendor to refer Process datasheet for tank and piping level settings and dimension
52 | 4. Fire arrestor will be supplied with breath valve
53
54
55
56

## EMERGENCY
DESIGN, PROCURREMENT AND CONSTRUCTION FOR NGHI SON PETROLEUM STORAGE PROJECT
|  |  |  | Datasheet.No: PVOIL.NS-DD-IN-DAS-001 | [9 empty] | Rev: A | Sheet: 5 of 5
DATASHEET FOR INSTRUMENT - EMERGENCY VALVE
Tag No. |  | : | See table below | [7 empty] | Client | : | PV OIL
Service |  | : | Tank Gauging | [7 empty] | Plant Location | : | Thanh hoa Province
P & ID No. |  | : | PVOIL.NS-FS-PR-PID-001 | [7 empty] | Facility | : | Nghi son Petroleum Storage
Specification No. |  | : | [8 empty] | No. of Units | : | N/A
SERVICE DESCRIPTION:
1 | GENERAL | Tag Name | [7 empty] | EMV-6001
2 |  | Line Number / Equipment No. | [7 empty] | TK-103
3 |  | Line size & Schedule | [7 empty] | -
4 |  | Equip./Vessel Protected | [7 empty] | DO Tank TK-103
5 |  | Valve Type | [7 empty] | Emergency Valve
6 |  | P&ID No | [7 empty] | PVOIL.NS-FS-PR-PID-001
7 | SERVICE CONDITION | Service | [7 empty] | Emergency relief
8 |  | Fluid & Fluid State | [7 empty] | E100
9 |  | Environment factor | [7 empty] | 1
10 |  | Vent discharge to | [7 empty] | To atmosphere
11 |  | Required Capacity | [5 empty] | Kg/h |  | -
12 |  | Pressure (Min/Max) |  |  |  |  | mm H2O |  |  | -25 to 200
13 |  | Temp.(Min/Max) | [6 empty] | °C | AMB
14 |  | Back Pressure: |  |  | Const./Variable |  |  |  |  | -
15 |  | Set Pressure |  |  |  |  | kg/cm2g |  |  | -
16 |  | Test Pressure | [7 empty] | VTA
17 |  | % Over Pressure |  |  |  | %Blown Down |  |  |  | -
18 |  | Compressibility Factor | [7 empty] | -
19 |  | Viscosity @ Rel Temp | [5 empty] | Cp |  | 0.91
20 |  | Vessel Wall Temp |  |  |  | Surf. Area cm2 |  |  |  | -
21 | VALVE | Type | [7 empty] | Conventional
22 |  | Nozzle | [7 empty] | Full nozzle
23 |  | Process Connection : Size & Rating | [7 empty] | 20" (API 650 Roof Manhole Connection)
24 |  | Facing & Finish | [7 empty] | FF
25 |  | Insulation Thickness | [7 empty] | N/A
26 | MATERIAL | Body | [7 empty] | ASTM A216 WBC
27 |  | Diaphram | [7 empty] | PTFE (TEFLON)
28 |  | Cushion | [7 empty] | Chloroprene Rubber
29 |  | Guide | [7 empty] | -
30 |  | Pallet/Seat | [7 empty] | SS 316
31 |  | Gasket | [7 empty] | No
32 |  | Bolts and Nuts | [7 empty] | No
33 |  | Tag name | [7 empty] | SS 316
34 | BASIS | Code | [7 empty] | API 2000
35 |  | Basis Of selection | [7 empty] | Operating
36 | PURCHASE | Manufacturer | [7 empty] | VTA
37 |  | Model | [7 empty] | VTA
38 |  | Certificate | [7 empty] | VTA
39
40 | Notes:
41 | 1.VTA: Vendor to Advise
42 | 2. 316SS tag stamped with Tag No., service, PO No. and manufacturers name plate in 15mm characters shall be permanently
43 | 3. Vendor to refer Process datasheet for tank and piping level settings and dimension
44
45
46
47
48